## Tension
Conductor sag and tension
The purpose of this calculation is to show how the simple expression given in equation R12 of AS/NZS7000 is able to calculate conductor tension if you know the span, sag and conductor weight
Conductor type |  | NITROGEN
Sag | D | 2804 | mm
Sag | D | 2.804 | m
Span | L | 120 | m
Conductor mass | m | 720 | kg/km | Looked up value in the Tables tab
Conductor weight | W | 7.0632 | N/m
Horizontal tension | H | 4534.1512 | N | Equation R12
Horizontal tension | H | 4.5342 | kN
Horizontal tension | H | 462.1969 | kg
Catenary constant | C | 641.9401 | m | Equation R1
|  |  |  | Equation R12 | Horizontal tension = 4.53kN
4,534N = | 7.06 x 120² |  |  | Equation R12
8 x 2.8
Modified equation R12
3m = | 7.06 x 120² |  |  | Modified equation R12
8 x 4,534
Equation R8
642m = | 4534.1512 |  |  | Equation R8
7.0632
This table uses equation R2 to calculate the parabolic conductor sag
Span distance | Sag
m | m
0 | 0
1.2 | 0.11104
2.4 | 0.21983
3.6 | 0.32639
4.8 | 0.43069
6 | 0.53276
7.2 | 0.63258
8.4 | 0.73016
9.6 | 0.8255
10.8 | 0.91859
12 | 1.0094
13.2 | 1.098
14.4 | 1.1844
15.6 | 1.2685
16.8 | 1.3504
18 | 1.43
19.2 | 1.5074
20.4 | 1.5826
21.6 | 1.6555
22.8 | 1.7261
24 | 1.7946
25.2 | 1.8607
26.4 | 1.9247
27.6 | 1.9864
28.8 | 2.0458
30 | 2.103
31.2 | 2.158
32.4 | 2.2107
33.6 | 2.2611
34.8 | 2.3094
36 | 2.3554
37.2 | 2.3991
38.4 | 2.4406
39.6 | 2.4799
40.8 | 2.5169
42 | 2.5516
43.2 | 2.5842
44.4 | 2.6144
45.6 | 2.6425
46.8 | 2.6683
48 | 2.6918
49.2 | 2.7132
50.4 | 2.7322
51.6 | 2.749
52.8 | 2.7636
54 | 2.776
55.2 | 2.7861
56.4 | 2.7939
57.6 | 2.7995
58.8 | 2.8029
60 | 2.804
61.2 | 2.8029
62.4 | 2.7995
63.6 | 2.7939
64.8 | 2.7861
66 | 2.776
67.2 | 2.7636
68.4 | 2.749
69.6 | 2.7322
70.8 | 2.7132
72 | 2.6918
73.2 | 2.6683
74.4 | 2.6425
75.6 | 2.6144
76.8 | 2.5842
78 | 2.5516
79.2 | 2.5169
80.4 | 2.4799
81.6 | 2.4406
82.8 | 2.3991
84 | 2.3554
85.2 | 2.3094
86.4 | 2.2611
87.6 | 2.2107
88.8 | 2.158
90 | 2.103
91.2 | 2.0458
92.4 | 1.9864
93.6 | 1.9247
94.8 | 1.8607
96 | 1.7946
97.2 | 1.7261
98.4 | 1.6555
99.6 | 1.5826
100.8 | 1.5074
102 | 1.43
103.2 | 1.3504
104.4 | 1.2685
105.6 | 1.1844
106.8 | 1.098
108 | 1.0094
109.2 | 0.91859
110.4 | 0.8255
111.6 | 0.73016
112.8 | 0.63258
114 | 0.53276
115.2 | 0.43069
116.4 | 0.32639
117.6 | 0.21983
118.8 | 0.11104
120 | -1.8208e-14
Horizontal tension = 4.53kN
H=(W𝐿^2)/8D
D=(W𝐿^2)/8𝐻
𝐶=𝐻/𝑊

## Details
Version | Created by | Date created | Reviewed by | Date reviewed | Comments
A | CNR | 2022-06-26
B
C
Purpose:
The purpose of this spreadsheet is to show how the simple expression given in equation R12 of AS/NZS7000 can be easily used to calculate conductor tension if you know the span, sag and conductor weight. This spreadsheet is intended for education purposes only. It has not been developed for the purpose of supporting commecial engineering activity and has not been through proper engineering review processes to validate its quality.
Limitations/Issues to be resolved:
References:
AS/NZS7000:2016
Cell colour conventions:
Input cell
Calculated cell (do not change)
Tabulated information or fixed variables (do not change)
Result/Output cell (<90% if representing a utilisation)
Result/Output cell (90-100% utilisation)
Result/Output cell (>100% utilisation)

## Tables
Tables
Name | Cross Sectional Area | Mass | Diameter | Modulus of Elasticity | Coefficient of Linear Expansion | Breaking Load | Stranding | Type | Standard
Unit | mm² | kg/km | mm | GPa | - / degs C | kN | No/mm
CHLORINE | 34.36 | 94.3 | 7.5 | 59 | 2.3e-05 | 8.18 | 7/2.50 | AAAC/1120 | AS/NZS 1531
FLOURINE | 49.48 | 134.9643 | 9 | 59 | 2.3e-05 | 11.8 | 7/3.00 | AAAC/1120 | AS/NZS 1531
HELIUM | 77.31 | 211 | 11.3 | 59 | 2.3e-05 | 17.6 | 7/3.75 | AAAC/1120 | AS/NZS 1531
IODINE | 124 | 339 | 14.3 | 59 | 2.3e-05 | 27.1 | 7/4.75 | AAAC/1120 | AS/NZS 1531
NEON | 209.8 | 576 | 18.8 | 56 | 2.3e-05 | 47.8 | 19/3.75 | AAAC/1120 | AS/NZS 1531
NITROGEN | 262 | 720 | 21 | 56 | 2.3e-05 | 62.2 | 37/3.00 | AAAC/1120 | AS/NZS 1531
OXYGEN | 337 | 930 | 23.8 | 56 | 2.3e-05 | 73.6 | 19/4.75 | AAAC/1120 | AS/NZS 1531
MARS | 77.3 | 212 | 11.3 | 56 | 2.3e-05 | 11.8 | 7/3.75 | AAC/1350 | AS/NZS 1531
BANANA | 77.3 | 268 | 11.3 | 83 | 1.93e-05 | 22.8 | 6/1/3.75 | ACSR/1350/GZ | AS/NZS 3607
BASEBALL | 77.3 | 254 | 11.3 | 79 | 2.01e-05 | 22.3 | 6/1/3.75 | ACSR/1350/AC | AS/NZS 3607
BANANA 1120 | 77.3 | 268 | 11.3 | 83 | 1.93e-05 | 27.9 | 6/1/3.75 | AACSR/1350/GZ | AS/NZS 3607
BASEBALL 1120 | 77.3 | 254 | 11.3 | 79 | 2.01e-05 | 27.6 | 6/1/3.75 | AACSR/1350/AC | AS/NZS 3607
HDCU 7/3.75 | 77.28 | 696 | 11.3 | 120 | 1.7e-05 | 28.8 | 7/3.75 | HDCU | AS 1746
SC/GZ 7/3.75 | 77.3 | 609 | 11.3 | 187 | 1.15e-05 | 91.3 | 7/3.75 | SC/GZ | AS 1222.1
SC/GC 7/3.75 | 77.28 | 515 | 11.3 | 157 | 1.29e-05 | 86.9 | 7/3.75 | SC/AC | AS 1222.2